Ventilation system…..

1.Requirements:

- A room contains an extractor fan and a fresh-air fan.

- Each fan is monitored by means of a flow sensor.

- The pressure in the room may rise above the atmospheric pressure.

- The fresh-air fan may only be switched on if the flow sensor signals the safe operational state of the extractor fan.

- A warning lamp indicates failure of one of the fans.

2.xLogic Solution:

The use of xLogic reduces the amount of switchgear. Thus, you save installation time and space in the control cabinet. You may even be able to use as a smaller control cabinet.

With xLogic you can also switch off of the fans sequentially after the system is switched off.

The system is switched on and off at the inputs I1 and I2. The fans are connected to outputs Q1 and Q2, the flow sensors are connected to the inputs I3 and I4. Blocks B07 and B10 are used to set the watchdog times after which the flow sensors should send a signal to the fault output Q3.

3.The function block program diagram is as following