Wire break evaluation / short circuit evaluation for Pt100/Pt1000 sensors

The measuring range is -50.0°C... +200.0°C.

If there is a wire break, there will be an infinite resistance of the connected sensor. xLogic will display 200°C.

If there is a short circuit, the resistance of the sensor is about zero. xLogic will display -50°C.

Values smaller than -50°C or larger than +200°C will not be indicated.

Therefore in the lower limit range the threshold smaller than -45.0°C can be evaluated as short circuit (B001) and in the upper limit range the threshold greater than 195.0°C can be evaluated as wire break (B002).

Therefore there is a defined range which indicates that there is something wrong with the sensor.

Warning:

Unsafe operating conditions can cause controllers to fail, resulting in unchecked operation of controlled devices.

Such hazardous events can cause death and/or serious injury and/or material damage. You must therefore provide an emergency stop function and electric or other redundant safety devices that are independent of your automation system.